**1.0 General**

**1.1** - Air filters shall be HEPA grade standard capacity air filters with waterproof micro glass fiber media, corrugated aluminum separators, urethane sealant, 16-gauge steel enclosing frame and one of the following: a poured-in-place seamless gasket, dovetail-cornered peel-and-stick neoprene gasket or gel seal.

**1.2** - Sizes shall be as noted on drawings or other supporting materials.

**2.0 Construction**

**2.1** - Filter media shall be one continuous pleating of micro-fine glass fiber media.

**2.2** - Pleats shall be uniformly separated by corrugated aluminum separators incorporating a hemmed edge to prevent damage to the media.

**2.3** - The media pack shall be potted into the enclosing frame with a fire-resistant urethane sealant.

**2.4** - The enclosing frame shall be of 16-gauge steel, with a zinc aluminum alloy finish, and shall be bonded to the media pack to form a rugged and durable enclosure. The filter shall be assembled without the use of fasteners to ensure no frame penetrations. Overall dimensional tolerance shall be correct within -1/8”, +0”, and square within 1/8”.

**2.5** - A (poured-in-place seamless gasket, dovetail-cornered peel-and-stick neoprene gasket or gel seal) shall be included on the downstream side of the enclosing frame to form a positive seal upon installation.

**3.0 Performance**

**3.1** - The filter shall have a tested efficiency of (99.97%, 99.99%, 99.999%)\* when evaluated according to IEST Recommended Practice.

**3.2** - Initial resistance to airflow shall not exceed 1.0” w.g.+/-10% at rated capacity.

**3.3** - Filter shall be rated by Underwriters Laboratories as UL-900 and UL-586.

**3.4** - The filter shall be capable of withstanding 10” w.g. without failure of the media pack.

**3.5** - Manufacturer shall provide evidence of facility certification to ISO 9001:2015.

**Supporting Data** - The filter shall be labeled as to tested efficiency, rated/tested cfm, pressure drop and shall be serialized for identification.

Filters shall be Camfil, Inc. Absolute XS or equal.

*\* Items in parentheses ( ) require selection.*

Sept/2024